Blue-White Flex-Pro Series models A3 and A4 Peristaltic Metering Pump

- METERING PUMP – Shall be a positive displacement, peristaltic type tubing pump with a brushless variable speed motor, non-spring loaded roller assembly located in the pumphead, integral tube failure detection system, and flexible tubing with attached connection fittings. Flex-Pro A3 model shall be capable of output volumes from 0.001 to 33.3 gallons per hour. Flex-Pro A4 model shall be capable of output volumes from 0.01 to 158.5 gallons per hour.

  - There shall be no valves, diaphragms, springs, or dynamic seals in the fluid path. Process fluid shall contact the pump tubing assembly and connection fittings only.

  - Capable of self priming at the rated maximum pressure of up to 125 PSI (8.6 bar).

  - Capable of running dry without damage.

  - Pump rollers shall be capable of operating in either direction at the maximum rated pump pressure.

  - Pump rollers shall be capable of operating in either direction without output variation.

  - Suction lift shall be 30 feet of water.

  - Pump shall have a two year manufacturer’s warranty that includes chemical damage to the pump head and roller assembly caused by a ruptured pump tube assembly.

- PUMPHEAD – Shall be a single, unbroken track with a clear removable cover

  - Tube failure detection sensors shall be wholly located in the pumphead. Tube failure detection system shall not trigger with water contact. Float switch type switches shall not be used. Process fluid waste ports or leak drains shall not be provided.

  - Squeeze rollers with encapsulated ball bearings shall be directly coupled to a one piece thermoplastic rotor. Four polymeric rollers shall be provided; two squeeze rollers for tubing compression shall be located 180 degrees apart and two guide rollers that do not compress the tubing shall be located 180 degrees apart. The roller diameters and occlusion gap shall be factory set to provide the optimum tubing compression; field adjustment shall not be required. Spring loaded or hinged rollers shall not be used.

  - Rotor assembly shall be installed on a D-shaped, chrome plated motor shaft and removable without tools.

  - For tubing installation and removal, rotor assembly shall be rotated by the motor drive at 6 RPM maximum when the pumphead cover is removed. Hand cranking of the rotor assembly shall not be required.

  - Pump head and tubing compression surface shall be corrosion resistant Valox thermoplastic.

  - The pump head cover shall be clear, annealed acrylic thermoplastic with an integral ball bearing fitted to support the overhung load on the motor shaft. Cover shall include an imbedded magnetic safety interlock which will limit the motor rotation speed to 6 RPM when removed.

  - Cover shall be positively secured to the pump head using a minimum of four thumb screws. Tools shall not be required to remove the pump head cover.

- PUMP TUBE ASSEMBLY

  - To ensure pump performance and accuracy, only tubing provided by the manufacturer is acceptable.

  - Pump tube shall be assembled to connection fittings of PVDF material.

  - Connection fittings shall be permanently clamped to the tubing with stainless steel clamps. To prevent tubing misalignment and ensure accuracy, fittings shall insert into keyed slots located in the pump head and secured in place by the pump head cover.

  - Connection fittings shall be 1/2” M/NPT. Alternate fittings shall accept 1/4” ID x 3/8” OD flexible tubing. (Engineer to specify)

  - Tube sizes and connections shall be measured in inches.

  - The following tube sizes shall be available:

- DRIVE SYSTEM – Shall be factory installed and totally enclosed in a NEMA 4X, (IP66) wash-down enclosure. Capable of operating on any input power from 110VAC to 240VAC, 50/60 Hz single phase supply without user configuration or selection switches.

  - Motor

    - Reversible, brushless DC gear motor rated for continuous duty.

    - Motor shall include overload protection.

    - The maximum gear motor RPM shall be 125 RPM.

  - Enclosure

    - Pressure cast aluminum with acidic liquid iron phosphate three-stage clean and coat pretreatment and exterior grade corrosion resistant polyester polyurethane powder coat.

    - Rated NEMA 4X (IP66).

    - Provided with 316SS floor/shelf level mounting brackets and hardware. Optional: provide extended height brackets for mounting pump 4.5 inches above grade level.  (Engineer to specify)

    - A wiring compartment shall be provided for connection of input/output signal wires and alarm output loads to un-pluggable type terminal block connectors. Terminal board shall be positively secured to the rear of the pump housing by two polymeric screws and fully enclosed by the wiring compartment cover. The terminal board shall not be disturbed by the removal of the wiring compartment cover. Ribbon cables shall not be used in the wiring compartment. Conduit hubs, liquid-tight connectors, connector through holes and tapped holes shall be sized in U.S. inches.

  - Control Circuitry.

    - Control circuitry shall be integral to the pump and capable of adjusting the pump motor speed from 0.05% to 100.00% in 0.01% increments less than 1% motor speed and in 0.1% increments greater than 1% motor speed (2,500:1 turndown ratio).

    - The pump output shall be capable of being manually controlled via front panel user touchpad controls. The pump motor speed shall be adjustable from 0.05% to 100.00% in 0.01% increments less than 1% motor speed and in 0.1% increments greater than 1% motor speed .

    - The pump output shall be capable of being remotely control via 4-20mA analog input. The input resolution shall be 0.01 of input value and capable of adjusting the pump motor speed from 0% to 100.0% motor speed in 0.1% increments. Four values shall be user configurable to define the low and high points on the output slope; a low input value, the required pump percentage of motor speed at the low input value, a high input value, the required pump percentage of motor speed at the high input value.

    - The pump output shall be capable of being remotely control via 0-10 VDC input. The input resolution shall be 0.01 of input value and capable of adjusting the pump motor speed from 0% to 100.0% motor speed in 0.1% increments. Four values shall be user configurable to define the low and high points on the output slope; a low input value, the required pump percentage of motor speed at the low input value, a high input value, the required pump percentage of motor speed at the high input value.

    - The pump output shall be capable of being remotely control via TTL/Cmos digital high speed pulse type input and an AC sine wave type pulse input in the range of 0 to 1000 Hz. The frequency resolution shall be 1 Hz and capable of adjusting the pump motor speed from 0% to 100.0% motor speed in 0.1% increments. Four values shall be user configurable to define the low and high points on the output slope; a low input value, the required pump percentage of motor speed at the low input value, a high input value, the required pump percentage of motor speed at the high input value.

    - The pump output shall be capable of being remotely control via pulse triggered batching. The pump shall accept a TTL/Cmos digital pulse type input and a contact closure type pulse input in the range of 1 to 9999 pulses per batch. The batch time shall be adjustable from 1 to 999.9 seconds. The pump motor speed during the batch shall be adjustable from 0% to 100.0% motor speed in 0.1% increments.

    - The pump shall include an internal cycle timer capable of automatically cycling the pump on and off. The pumping total cycle time shall be adjustable from 1 to 999.9 seconds. The pumping on time during the cycle shall be adjustable from 1 to 999.9 seconds. The pump motor speed during the cycle shall be adjustable from 0% to 100.0% motor speed in 0.1% increments.

    - The pump shall be capable of dispensing upon demand. The dispensing shall be manually triggered by pressing the front panel start button or by inputting a contact closure. The dispensing volume shall be adjustable from 1 to 9999 milliliters. The pump motor speed during the dispensing cycle shall be adjustable from 0% to 100.0% motor speed in 0.1% increments.

    - The pump shall be capable of automatically calculating the pump motor speed required to achieve a part per million dosing output that is proportional to a fixed system flow rate. The pump shall permit the user to input the dispensing chemical percentage concentration from 0% to 100.0% in 0.1% increments. The pump shall permit the user to input the dispensing chemical specific gravity from 0.1 to 9.9 in 0.1 increments. The pump shall permit the user to input the fixed system flow rate from 1.0 to 9999.9 liters per minute in 0.1 liters per minute increments. The pump shall permit the user to input the required dosing parts per million (PPM) from 0.1 to 100.0 in 0.1 increments.

    - The pump shall be capable of automatically calculating the pump motor speed required to achieve a part per million dosing output that is proportional to a variable system flow rate. The pump shall permit the user to input the dispensing chemical percentage concentration from 0% to 100.0% in 0.1% increments. The pump shall permit the user to input the dispensing chemical specific gravity from 0.1 to 9.9 in 0.1 increments. The pump shall permit the user to input a K-factor in pulses per liter from a sensor in the water system that outputs a high speed digital pulse from 0 to 1000 Hz that is proportional to the system water flow velocity. The pump shall permit the user to input the required dosing parts per million (PPM) from 0.1 to 100.0 in 0.1 increments.

    - Provide a 10-button front panel user touchpad control for stop/start, configuration menu access and navigation, operating mode selection, auto priming, display options selection, and reverse direction.

    - Provide a multi-color VGA graphic LCD display for menu driven configuration settings, pump output value, service alerts, tube failure detection (TFD) system and flow verification system (FVS) alarms status, remote input signal values, tubing life timer value. Display color shall be green when indicating normal operation, blue when in stand-by, and red to indicate an alarm condition exists.

    - Provide for remote stop/start pump via 6-30 VDC powered loop or non-powered contact closure loop.

    - Provide a user selectable 4-20mA and 0-1000Hz output signal which are scalable and proportional to pump output volume.

    - Provide four contact closure alarm outputs. Three rated at 1A-115VAC, 0.8A-30VDC and one rated at 6A-250VAC, 5A-30VDC. Each alarm output shall be assignable to any of the following pump functions: TFD system, FVS system, motor run/stop, motor failed to respond to commands, input signal failure, output signal failure, remote/local control setting, or monitor which of the nine different pump operating modes is currently active.

    - Provide a four digit password protected configuration menu.

    - Provide a flow verification system with programmable alarm delay time from 1-255 seconds. FVS system shall monitor the FVS flow sensor while pump is running only. System shall not monitor pump while not running.

- FLOW VERIFICATION SENSOR – Shall output high speed digital pulse signal, while pump is running only, to verify chemical injection.

  - Flow verification sensor shall be a paddlewheel type sensor.

  - Sensor body, paddle, lens cap, and axle material shall be PVDF.

  - 1/2” M/NPT connections shall be PVC. Alternate inlet and outlet fitting connections shall accept 1/4” ID x 3/8” OD flexible tubing and shall be PVDF. (Engineer to specify)

  - Sensor operating range shall be as follows: (Engineer to specify)

Code		Operating Range (ounces per minute)

101			1.0-10.0

201			3.5-35.0

301			7.0-70.0

401			10.0-100.0

501			17.0-170.0

601			24.0-240.0

- SAFETY

  - The pump shall be listed to UL standard 778 as a motor operated pump and CSA standard C22.2 as process control equipment.

  - Tube Failure Detection (TFD) system sensors shall be wholly located in the pumphead. TFD system will stop the pump within three seconds of leak detection. To prevent false alarms due to rain, wash-down, condensation, etc., tube failure detection system shall not trigger with water contact. Process fluid waste ports or leak drains shall not be provided.

  - Pumphead cover shall include an imbedded magnetic safety interlock which will stop the pump when removed. Pump rotor speed shall be limited to 6 RPM when cover is removed.

  - Secondary user confirmation input required for motor reversal, tube life timer reset, and factory default configuration reset.

- Manufacturer

  - The pump shall be Blue-White ProSeries Flex-Pro series peristaltic pumps, manufactured in the U.S.A. by Blue-White Industries.